## Slide 1
Underground Infrastructure Mapping
Charles W. McCrackin, M.S., P.G.

## Slide 2: What’s in the Subsurface?
Underground Utilities - telecommunication lines, underground power, gas lines, water lines, sanitary sewer, storm water pipes, fiber optics, duct banks, groundwater wells, etc.
Underground Storage Tanks – petroleum tanks, septic tanks, waste water tanks, catch basins, etc.
Septic Systems – drain-fields, sanitary sewer systems, etc.
Buried Foundations – building foundations, vertical piles, drilled shafts, sheet piles, sea walls, tie backs, etc.
Fill Material - landfill, buried debris, slag pits, heterogeneous materials, infill material, organic laden soils from poor site development, clays, till, etc.

## Slide 3: What to consider when mapping the subsurface?
Target Type
Target Depth
Soil Conditions
Water Table
Above Ground Structures

## Slide 4: What type of geophysical methods are used to map buried infrastructure?
Ground Penetrating Radar (GPR)
Electromagnetics (EM)
Electrical Resistivity (ER)
Magnetics (Mag)
Seismics

## Slide 5: Ground Penetrating Radar (GPR)
Transmits and receives electromagnetic pulses (high frequency microwave energy) into the ground and detects differences in the dielectric properties (ability of materials to hold a charge) of the subsurface materials.
Pros
Highly effective in resistive sandy soils
Very high resolution geophysical method
Cons
Limited depth of penetration
Depth of penetration affected by conductive soils (clays, organics, leachate)
Applications
Underground Utilities
Buried Debris
Landfill Delineation
Underground Storage Tanks
Fill Depth/Thickness
Void Detection
Plume Mapping
Structural Elements in Concrete (Rebar)
Courtesy of USDA website

## Slide 6: Electrical Resistivity (ER)
Measures potential differences of the subsurface materials by passing electrical current into the ground and measuring the potential difference between two points.
Pros
Most effective in conductive clayey soils
Capable of profiling deeper depth of penetration (in excess of 100 feet under certain soil conditions and line length)
Has a lateral zone of influence
Highly effective for hydrological studies
Cons
Lower resolution geophysical method
Susceptible to noise and interference
Applications
Buried Debris
Landfill Delineation
Underground Storage Tanks
Fill Depth/Thickness
Void Detection
Plume Mapping

## Slide 7: Electromagnetics (EM)
A primary EM field is created and is quickly shut-off creating a secondary field. The secondary EM field that has been created is then recorded. (Non-ferrous metal such as: brass, aluminum, and tin are not detected)
Pros
Capable of mapping large survey areas over a relatively short amount of time
Not influenced by smaller discrete buried metal
Cons
Non-ferrous objects are not detected.
Maximum depth of detection is approximately 15 feet
May be influenced by interference from above ground metal structures
Applications
Landfill Delineation
Utility Mapping
Underground Storage Tank (UST) Locating
Unexploded Ordinance Mapping
Buried Infrastructure Mapping
Courtesy of Geonics, LTD

## Slide 8: Magnetics (MAG)
Pros
Capable of mapping large survey areas over a relatively short amount of time
Not influenced by smaller discrete buried metal
Cons
Non-ferrous objects are not detected.
Depth of detection is dependent on size of the buried ferrous object.
May be influenced by interference from above ground metal structures and overhead power lines
Susceptible to diurnal changes in the Earth’s magnetic field (corrections must be made)
Applications
Landfill Delineation
Utility Mapping
Underground Storage Tank (UST) Locating
Buried Infrastructure Mapping
Geologic Mapping and Mining
Courtesy of EPA website
Courtesy of ASM website
Measurements are made to record the spatial variations in the earth’s total magnetic field

## Slide 9: Seismics
Seismic waves are transmitted through the subsurface to access the P (Longitudinal/Compressional) and S (Transverse/Shear) waves behavior so that the elastic (stress and strain) properties of the material can be used to determined (E-Young’s modulus, µ-Poisson’s ratio, K-bulk modulus, and G-rigidity modulus) which give us wave velocities or p-density of the subsurface materials.
Applications
Mapping Top of Rock
Crosshole Geophysics
Assessing Strength of Subsurface Materials for Building Foundations/Critical Infrastructure (e.g., Dam and Bridge Construction)
Geologic and Engineering Studies
Pros
Numerous Seismic Methods for shallow and deep mapping
Refraction and MASW surveys highly effective in the upper 100 ft.
Provides information directly related to material density and easily correlated to relative “N” values
Cons
Can be field extensive and requires considerable data processing
Depending on the Seismic method deployed may have various limitations with noise/interference to consider at each site

## Slide 10: Complimentary Methods
Conventional Utility Locator
Pile Integrity Test
Thermal Imaging Camera
Video Inspection

## Slide 11: Multi-Level Approach
Courtesy of Geoview
Why use more than one method?
Each geophysical method detects various soil properties
Allows for data comparison and correlation
Provides more information about the subsurface for improved subsurface site characterization

## Slide 12: 2D vs 3D Subsurface Mapping
2D-Primary Geophysical Profiling Method
3D-Hot Topic for Current Geophysical Research
2D Applications
Still the most widely used and most cost effective survey technique for all geophysical methods
Highly effective when correlated with 1D ground truth data such as SPT and CPT data
Provides cross-sectional data in between confirmation borings to confirm the general subsurface profile
Can be converged with parallel or orthogonal 2D transects to provide pseudo-3D information about the subsurface
3D Applications
Generally relegated to only 2 or 3 geophysical methods (i.e., Ground Penetrating Radar, Electrical Resistivity and some research in 3D MASW seismic surveying)
Generally constrained to smaller survey areas which require very high resolution (i.e., Imaging of Concrete Structures-rebar mapping, void detection, utility mapping, roadway mapping and applications in archaeology)

## Slide 13: 2D vs 3D Data
Transect 2 (2D Inversion)
Transect 2 (3D Inversion)
McCrackin, Kruse, and Van Beynen, 2012

## Slide 14: 2D vs 3D GPR Data Examples

## Slide 15: 2D vs 3D ERT Data Examples

## Slide 16: 2D vs 3D MASW Seismic Data Examples
Park and Taylor, 2009

## Slide 17: What to expect when mapping the subsurface?
Expect the Unexpected !
Buried Foundations
Underground Utilities
Organics
Clays
Till
Near-surface water table
Underground Storage Tanks
Sheet Piles
Tie Backs
Buried Debris
Heterogeneous Fill Material
Surface Obstructions

## Slide 18: Potential Issues to Consider
Accessibility and site access (Dense vegetation or debris at the surface)
Heavily reinforced concrete at the site with metal or wire mesh
Highly conjested near-surface infrastructure masking deeper buried structures
Conductive soils or surface material
Shallow water table
Electrical or Seismic noise present

## Slide 19: Expectations and Realistic Goals
Geophysics - is a non-destructive, non-invasive tool that requires ground truth data to fully understand and provide accurate, meaningful geophysical results
Garbage in > Garbage out
Meaningful subsurface data will be correlated with subsurface testing (e.g., SPT, Hand Auger or Test Pit data)
Be cautious of over reaching geophysical results with no supporting ground truth information
Geophysical surveys rarely have conclusive results by themselves
Geophysical surveys are an effective tool to identify “Areas of Interest” or “Features” to further investigate and confirm
Geophysical surveys narrow the investigation and help provide information about the subsurface properties and material characteristics that must be identified with exploratory destructive testing

## Slide 20: Ground Truth, Ground Truth, Ground Truth…
Physical Exploratory Testing is often destructive, can be costly, and may require multiple locations
Geophysics provides a 2D and sometimes 3D mapping approach to limit the amount of destructive testing
Be very selective with subsurface testing locations (testing inside and outside areas of interest can sometimes offer great insight)
Understand that Physical 1D testing methods such as SPT and CPT data may not be a good representation of the entire site (i.e., such methods only provide a 2”-3” diameter sampling tube or resistance tip)
Consider other options such as video line inspections of underground utilities, vacuum extraction or hand trenching in highly congested/sensitive areas.
DON’T FORGET THE LOCAL ONE CALL SYSTEM!

## Slide 21: Advanced Subsurface Mapping and Data Management
GIS Mapping
Geospatial Data Analysis
Infrastructure and Data Management

## Slide 22: Questions ?